COMPUTER ROOM AC UNITS

## CLOSE CONTROL LARGE SYSTEMS RANGE

- The close control large systems range has 4 unit sizes providing nominal capacities of 60 - 120kW.

- Units are available in chilled water and dual chilled water versions.

- Units are available in upflow, downflow and downflow front discharge displacement airflow configurations.

- Standard DX units on R407C with an option on R410A.

- Standard units have forward curved belt driven fans, with an option on backward curved direct drive EC fans.

- BMS interfaces available are MODBUS, BACnet, MSTP, BACnet IP, SNMP IP, LON & Trend.

- Full range of options available including:

  - Reheat of various types

  - Humidifiers

  - Electronic expansion valves

  - Discharge and acoustic plenums

  - Floorstands and dampers

  - Upgraded filter class

  - Fire and smoke detectors

  - Water detection

  - Condensate pumps

| Model |  | 60 | 80 | 100 | 120 |
| --- | --- | --- | --- | --- | --- |
| Air Volume | m3/hr | 15500 | 19000 | 25000 | 29000 |
| Total Capacity - 4Row | kW | 49.6 | 62.7 | 85.1 | 101.5 |
| Sensible Capacity - 4Row | kW | 49.4 | 62.4 | 85.1 | 101.5 |
| Total Capacity - 6Row | kW | 62.3 | 77.6 | 103.9 | 122.6 |
| Sensible Capacity - 6Row | kW | 57.5 | 70.4 | 103.9 | 110.4 |
| Unit Length | mm | 1660 | 2000 | 2500 | 2800 |

- Nominal Capacity based on 22°C & 50%RH return air, and for chilled water an entering temperature of 6°C.

- Unit measurements for depth and height are 875mm and 1980mm respectively.