COMPUTER ROOM AC UNITS

## CLOSE CONTROL MODULAR RANGE

- The close control twin circuit air cooled range has 4 module sizes providing nominal capacities of 10 - 40kW. Twin circuit units are created by using 2x modules providing nominal capacities of 20 - 80kW. Modules are connected with interconnecting power and control harnesses.

- Units are available in air, water, glycol, freecooling, chilled water and dual cooled versions.

- Units are available in upflow, downflow and downflow front discharge displacement airflow configurations.

- Standard DX units on R407C with an option on R410A.

- Condensers and drycoolers can be selected for 30, 35, 40, 45 & 50 ambients.

- Standard units have forward curved belt driven fans, with an option on backward curved direct drive EC fans.

- BMS interfaces available are MODBUS, BACnet, MSTP, BACnet IP, SNMP IP, LON & Trend.

- Full range of options available including:

  - Reheat of various types

  - Humidifiers

  - Electronic expansion valves

  - Discharge and acoustic plenums

  - Floorstands and dampers

  - Upgraded filter class

  - Fire and smoke detectors

  - Water detection

  - Condensate pumps

| Model |  | 10 | 15 | 20 | 25 | 30 | 35 | 40 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Air Volume | m3/hr | 3000 | 4500 | 6000 | 7500 | 9000 | 10500 | 12000 |
| Total Capacity - DX | kW | 10.5 | 15.3 | 21.4 | 23.9 | 32.2 | 34.9 | 40.9 |
| Sensible Capacity - DX | kW | 9.8 | 13.8 | 19.9 | 21.8 | 29.4 | 31.6 | 37.7 |
| Total Capacity - CW | kW | 11.6 | 16.0 | 22.5 | 26.8 | 30.8 | 34.6 | 40.7 |
| Sensible Capacity - CW | kW | 10.5 | 15.9 | 21.1 | 25.4 | 30.7 | 34.5 | 40.6 |
| Unit Length | mm | 775 | 775 | 1208 | 1208 | 1308 | 1308 | 1500 |

- Nominal Capacity based on 22°C & 50%RH return air, and for chilled water an entering temperature of 6°C.

- Unit measurements for depth and height are 775mm and 1980mm respectively.