COMPUTER ROOM AC UNITS

## CLOSE CONTROL SMALL SYSTEMS RANGE

- The close control small systems range has 2 unit sizes providing nominal capacities of 6 - 18kW.

- Units are available in air cooled, chilled water and dual cooled versions.

- Units are available in upflow, downflow and downflow front discharge displacement airflow configurations.

- Standard DX units on R407C with an option on R410A.

- Condensers can be selected for 30, 35, 40, 45 & 50 ambients.

- Standard units have forward curved belt driven fans, with an option on backward curved direct drive EC fans.

- BMS interfaces available are MODBUS, BACnet, MSTP, BACnet IP, SNMP IP, LON & Trend.

- Full range of options available including:

  - Reheat of various types

  - Humidifiers

  - Electronic expansion valves

  - Discharge and acoustic plenums

  - Floorstands and dampers

  - Upgraded filter class

  - Fire and smoke detectors

  - Water detection

  - Condensate pumps

| Model |  | 06 | 12 | 18 |
| --- | --- | --- | --- | --- |
| Air Volume | m3/hr | 1800 | 3600 | 5400 |
| Total Capacity - DX | kW | 7.2 | 13.0 | 17.4 |
| Sensible Capacity - DX | kW | 6.6 | 11.9 | 15.8 |
| Total Capacity - CW | kW | 7.0 | 12.2 | 18.3 |
| Sensible Capacity - CW | kW | 6.4 | 12.1 | 18.3 |
| Unit Length | mm | 600 | 600 | 775 |

- Nominal Capacity based on 22°C & 50%RH return air, and for chilled water an entering temperature of 6°C.

- Unit measurements for depth and height are 600mm and 1980mm respectively, except for the 18 model which is 775 in depth.